## Earth Electrode Test
EARTH ELECTRODE RESISTANCE TEST REPORT
Fall-of-potential method, 62 % rule with 52 / 62 / 72 % plateau check
Enter data in the blue-on-yellow cells. Grey cells are calculated and locked (sheet protection has no password: Review > Unprotect Sheet).
1. Job and test details
Customer / site |  |  |  | Electrode ID / tag
Electrode type and description |  |  |  | Test date
Soil condition at test |  |  |  | Last rainfall (date or days ago)
Largest dimension of electrode L (m) |  |  |  | Distance from electrode E to current spike C: D (m)
Seasonal correction factor (default 1.0) |  |  |  | Permitted earth resistance (Ω)
Test instrument model |  |  |  | Serial number and calibration due
Tested by |  |  |  | Witnessed or reviewed by
Spacing check: minimum D for this electrode (m)
2. Readings along the line from E to C
Position of P (% of D) | Distance of P from E (m) | Reading R (Ω) | Role
10%
20%
30%
40%
50%
52% |  |  | Check
62% |  |  | Reported value
72% |  |  | Check
80%
90%
Take the readings with P moved in steps while E and C stay fixed. The 52, 62 and 72 % rows are linked to the Reference sheet and drive the plateau check.
3. Result
Reading at 52 %
Reading at 62 %
Reading at 72 %
Largest difference from the 62 % reading
Plateau check
Seasonal correction factor applied | 1
EARTH RESISTANCE REPORTED (Ω)
Against permitted value
Remarks and recommended action
Signature and date: tester |  |  |  | Reviewer

## Soil and Rod
SOIL RESISTIVITY (WENNER) AND ROD ESTIMATE
Four-pin Wenner method with exact depth correction, plus a single-rod resistance estimate for comparison with the measurement
Enter data in the blue-on-yellow cells. Grey cells are calculated and locked (sheet protection has no password: Review > Unprotect Sheet).
1. Test details
Customer / site |  |  |  | Test date
Traverse direction and location |  |  |  | Instrument and serial
Probe depth b (m) |  | Depth to which each pin is driven. Keep it small compared with the spacing.
2. Readings and apparent resistivity
Spacing a (m) | Reading R (Ω) | b / a | Resistivity, exact (Ω·m) | Resistivity, 2 pi a R (Ω·m) | Difference exact vs simple
Average resistivity (Ω·m) |  |  | Apparent resistivity at spacing a represents soil down to a depth of the order of a. A resistivity that changes strongly with spacing suggests layered soil.
Lowest / highest (Ω·m)
Highest divided by lowest
3. Single vertical rod estimate (for comparison)
Resistivity to use (Ω·m) |  | Leave blank to use the Wenner average above.
Resistivity used (Ω·m)
Rod length in the soil L (m)
Rod diameter (mm)
Estimated resistance of one rod (Ω)
Measured earth resistance (Ω) |  | Linked from the earth electrode test sheet.
Measured against estimate
Informational only. The estimate assumes uniform soil and one vertical rod, so a difference of tens of percent is common. Large differences point to layered soil, rock, moisture or interference worth investigating.

## Earth Electrode Test (Example)
EARTH ELECTRODE RESISTANCE TEST REPORT
Fall-of-potential method, 62 % rule with 52 / 62 / 72 % plateau check
EXAMPLE with made-up data, to show the expected format. Use the blank sheet for your own report.
1. Job and test details
Customer / site | Demo Plant, Howrah |  |  | Electrode ID / tag | EP-3 main earth rod
Electrode type and description | Copper-bonded rod, 3 m x 16 mm, in a pit |  |  | Test date | 2026-10-18
Soil condition at test | Damp |  |  | Last rainfall (date or days ago) | 3 days ago
Largest dimension of electrode L (m) | 3 |  |  | Distance from electrode E to current spike C: D (m) | 40
Seasonal correction factor (default 1.0) | 1 |  |  | Permitted earth resistance (Ω) | 5
Test instrument model | CIE DET-2000 |  |  | Serial number and calibration due | Sample serial, cal due Mar 2027
Tested by | A. Sample |  |  | Witnessed or reviewed by | B. Sample
Spacing check: minimum D for this electrode (m) | 15 | Valid - D is at least 5 x L
2. Readings along the line from E to C
Position of P (% of D) | Distance of P from E (m) | Reading R (Ω) | Role
10% | 4 | 12
20% | 8 | 15.5
30% | 12 | 17.6
40% | 16 | 18.8
50% | 20 | 19.5
52% | 20.8 | 19.6 | Check
62% | 24.8 | 19.8 | Reported value
72% | 28.8 | 20.1 | Check
80% | 32 | 21.5
90% | 36 | 27
Take the readings with P moved in steps while E and C stay fixed. The 52, 62 and 72 % rows are linked to the Reference sheet and drive the plateau check.
3. Result
Reading at 52 % | 19.6
Reading at 62 % | 19.8
Reading at 72 % | 20.1
Largest difference from the 62 % reading | 1.515%
Plateau check | Valid - the three readings agree within 5 %
Seasonal correction factor applied | 1
EARTH RESISTANCE REPORTED (Ω) | 19.8
Against permitted value | FAIL - 19.80 Ω is above 5.00 Ω
Remarks and recommended action | Example only. The 52, 62 and 72 % readings agree within 5 %, so the plateau is valid. The result is above the 5 Ω target, so add rods or treat the soil, then retest. Also retest in the dry season.
Signature and date: tester |  |  |  | Reviewer

## Soil and Rod (Example)
SOIL RESISTIVITY (WENNER) AND ROD ESTIMATE
Four-pin Wenner method with exact depth correction, plus a single-rod resistance estimate for comparison with the measurement
EXAMPLE with made-up data, to show the expected format. Use the blank sheet for your own report.
1. Test details
Customer / site | Demo Plant, Howrah |  |  | Test date | 2026-10-18
Traverse direction and location | North to south along the cable route |  |  | Instrument and serial | CIE DET-2000
Probe depth b (m) | 0.2 | Depth to which each pin is driven. Keep it small compared with the spacing.
2. Readings and apparent resistivity
Spacing a (m) | Reading R (Ω) | b / a | Resistivity, exact (Ω·m) | Resistivity, 2 pi a R (Ω·m) | Difference exact vs simple
1 | 9.87 | 0.2 | 66.101 | 62.015 | -6.181%
2 | 4.77 | 0.1 | 60.9744 | 59.9416 | -1.694%
4 | 2.31 | 0.05 | 58.3096 | 58.0566 | -0.4339%
8 | 1.17 | 0.025 | 58.8749 | 58.8106 | -0.1091%
16 | 0.61 | 0.0125 | 61.3407 | 61.3239 | -0.02733%
Average resistivity (Ω·m) | 61.1201 |  | Apparent resistivity at spacing a represents soil down to a depth of the order of a. A resistivity that changes strongly with spacing suggests layered soil.
Lowest / highest (Ω·m) | 58.3096 | 66.101
Highest divided by lowest | 1.1336
3. Single vertical rod estimate (for comparison)
Resistivity to use (Ω·m) |  | Leave blank to use the Wenner average above.
Resistivity used (Ω·m) | 61.1201
Rod length in the soil L (m) | 3
Rod diameter (mm) | 16
Estimated resistance of one rod (Ω) | 20.4708
Measured earth resistance (Ω) | 19.8 | Linked from the earth electrode test sheet.
Measured against estimate | -3.277%
Informational only. The estimate assumes uniform soil and one vertical rod, so a difference of tens of percent is common. Large differences point to layered soil, rock, moisture or interference worth investigating.

## Reference
REFERENCE: constants, formulas and sources
Every constant used by the report sheets is listed here once. Blue cells can be edited.
Enter data in the blue-on-yellow cells. Grey cells are calculated and locked (sheet protection has no password: Review > Unprotect Sheet).
A. Constants used in the formulas
Item | Value | Unit | Basis
First check position of the potential spike P | 52% | % of D | 52 / 62 / 72 % readings are compared to confirm the plateau (fall-of-potential, 62 % method)
Main position of the potential spike P | 62% | % of D | 61.8 % of D is the theoretical position, commonly rounded to 62 %
Second check position of the potential spike P | 72% | % of D | See first check position
Allowed spread of the three readings about the 62 % reading | 5 | % | A practical acceptance figure, not a limit from a standard. Tighten or relax to suit the job.
Minimum E to C distance D as a multiple of the largest electrode dimension | 5 | x L | Common field guide. Larger electrodes and grids may need more. Not a limit from a standard.
B. Formulas
Fall of potential | P distance = fraction x D. The reported earth resistance is the reading at 62 % of D, multiplied by the seasonal factor you enter (default 1).
Wenner apparent resistivity | rho = 4 x pi x a x R / (1 + 2a / SQRT(a^2 + 4b^2) - a / SQRT(a^2 + b^2)), with a = probe spacing, b = probe depth, R = tester reading. For b much smaller than a this reduces to rho = 2 x pi x a x R.
Single vertical rod estimate | R = rho / (2 x pi x L) x (LN(4L / r) - 1), with L = rod length in the soil and r = rod radius (Dwight formula, uniform soil, L much larger than r).
C. Sources, assumptions and limits of use
Sources: IEEE Std 81-2012, Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Surface Potentials of a Grounding System (fall-of-potential method, 62 % rule, Wenner method). Rod formula: H. B. Dwight, 1936. Check against the edition and method your specification names.
The 62 % rule assumes reasonably uniform soil and an electrode that is small compared with the E to C distance. In layered soil, or near buried metalwork, results can differ. Where the three readings do not agree, increase D and repeat.
Keep the P and C spikes in line with the electrode, away from buried pipes and cables, and in undisturbed soil. Disconnect the electrode from the installation if the instrument procedure requires it.
Earth resistance varies with season and soil moisture. Record the soil condition and last rainfall. The seasonal factor is yours to set from site or utility practice and defaults to 1.0.
The rod estimate is an indication for a single vertical rod in uniform soil. It does not replace a measurement and has no pass or fail limit.