## Report
INSULATION RESISTANCE TEST REPORT
Timed test (15 s, 30 s, 45 s, 60 s, 10 min) with temperature correction, DAR, polarization index and IEEE 43 minimums
Enter data in the blue-on-yellow cells. Grey cells are calculated and locked (sheet protection has no password: Review > Unprotect Sheet).
1. Job and machine details
Customer / site |  |  |  | Equipment ID / tag
Machine / cable description |  |  |  | Test date
Rated line voltage (kV) |  |  |  | Winding class (sets minimum IR)
Thermal class of insulation |  |  |  | Test voltage applied (V DC)
Winding / insulation temperature (°C) |  |  |  | Ambient temperature (°C) and humidity (%)
Test instrument model |  |  |  | Instrument serial number and calibration due
Tested by |  |  |  | Witnessed or reviewed by
2. Timed readings and calculated values
Connection tested (for example U to E, V and W earthed) | 15 s (MΩ) | 30 s (MΩ) | 45 s (MΩ) | 60 s (MΩ) | 10 min (MΩ) | Leakage at 1 min (µA) | Temp. factor Kt | IR 1 min at 40 °C (MΩ) | DAR (60 s / 30 s) | PI (10 min / 1 min)
Kt = 0.5^((40 - T) / 10). IR at 40 °C = IR at 1 min x Kt. Leakage = test voltage / IR at 1 min. Add rows by copying the last row if you test more connections.
3. Limits for this machine
Minimum IR at 40 °C, 1 min (MΩ) |  | IEEE 43-2013: kV + 1, or 100, or 5 MΩ depending on the winding class selected above.
Minimum polarization index |  | IEEE 43-2013: 1.5 for thermal class A, 2.0 for B, F and H.
Recommended test voltage (IEEE 43-2013) |  |  |  | from / to, V DC (band number is the row in Reference section B)
Test voltage used against recommendation
4. Evaluation per connection
Connection | IR 1 min at 40 °C (MΩ) | Minimum IR (MΩ) | IR check | DAR class | PI | PI class (guide) | Minimum PI | PI check | Result | Remarks
5. Result
Overall result
Lowest IR at 40 °C across connections (MΩ)
Lowest PI across connections
Remarks and recommended action
Signature and date: tester |  |  |  |  | Reviewer
Method notes
1. Isolate and disconnect the winding or cable, and discharge it before and after the test. Keep leads clear of earth and of each other, and use the guard terminal where surface leakage may affect the reading.
2. Apply the test voltage continuously for 10 minutes and note the readings at the times shown. A hand-driven tester cannot hold voltage that long, so use a motor-driven or digital instrument for PI.
3. Record the winding temperature, not just the ambient temperature. Kt is an approximation and is most reliable when readings are compared at similar temperatures.
4. PI is not meaningful when the 1-minute reading is above about 5000 MΩ. Judge on the absolute reading and the trend instead.
5. Limits come from the Reference sheet (IEEE 43-2013 for rotating machines). Use the stricter of these and your plant or customer specification.

## Example
INSULATION RESISTANCE TEST REPORT
Timed test (15 s, 30 s, 45 s, 60 s, 10 min) with temperature correction, DAR, polarization index and IEEE 43 minimums
EXAMPLE with made-up data, to show the expected format. Use the blank sheet for your own report.
1. Job and machine details
Customer / site | Demo Plant, Howrah |  |  | Equipment ID / tag |  | P-101 pump motor
Machine / cable description | 415 V, 55 kW induction motor, random-wound stator |  |  | Test date |  | 2026-10-18
Rated line voltage (kV) | 0.415 |  |  | Winding class (sets minimum IR) |  | Random-wound, or form-wound below 1 kV (5 MΩ)
Thermal class of insulation | F |  |  | Test voltage applied (V DC) |  | 500
Winding / insulation temperature (°C) | 32 |  |  | Ambient temperature (°C) and humidity (%) |  | 30 °C / 68 %
Test instrument model | CIE DIT-2500 |  |  | Instrument serial number and calibration due |  | Sample serial, cal due Mar 2027
Tested by | A. Sample |  |  | Witnessed or reviewed by |  | B. Sample
2. Timed readings and calculated values
Connection tested (for example U to E, V and W earthed) | 15 s (MΩ) | 30 s (MΩ) | 45 s (MΩ) | 60 s (MΩ) | 10 min (MΩ) | Leakage at 1 min (µA) | Temp. factor Kt | IR 1 min at 40 °C (MΩ) | DAR (60 s / 30 s) | PI (10 min / 1 min)
U to E (V, W earthed) | 180 | 230 | 270 | 300 | 900 | 1.6667 | 0.57435 | 172.3048 | 1.3043 | 3
V to E (U, W earthed) | 170 | 220 | 260 | 285 | 860 | 1.7544 | 0.57435 | 163.6895 | 1.2955 | 3.0175
W to E (U, V earthed) | 175 | 225 | 262 | 290 | 870 | 1.7241 | 0.57435 | 166.5613 | 1.2889 | 3
Kt = 0.5^((40 - T) / 10). IR at 40 °C = IR at 1 min x Kt. Leakage = test voltage / IR at 1 min. Add rows by copying the last row if you test more connections.
3. Limits for this machine
Minimum IR at 40 °C, 1 min (MΩ) | 5 | IEEE 43-2013: kV + 1, or 100, or 5 MΩ depending on the winding class selected above.
Minimum polarization index | 2 | IEEE 43-2013: 1.5 for thermal class A, 2.0 for B, F and H.
Recommended test voltage (IEEE 43-2013) | 1 | 500 | 500 | from / to, V DC (band number is the row in Reference section B)
Test voltage used against recommendation | Within recommended range
4. Evaluation per connection
Connection | IR 1 min at 40 °C (MΩ) | Minimum IR (MΩ) | IR check | DAR class | PI | PI class (guide) | Minimum PI | PI check | Result | Remarks
U to E (V, W earthed) | 172.3048 | 5 | Meets minimum | Acceptable | 3 | Good | 2 | Meets minimum | PASS
V to E (U, W earthed) | 163.6895 | 5 | Meets minimum | Acceptable | 3.0175 | Good | 2 | Meets minimum | PASS
W to E (U, V earthed) | 166.5613 | 5 | Meets minimum | Acceptable | 3 | Good | 2 | Meets minimum | PASS
5. Result
Overall result | PASS - all 3 connections meet the minimums
Lowest IR at 40 °C across connections (MΩ) | 163.6895
Lowest PI across connections | 3
Remarks and recommended action | Example only. All three windings above the minimum with healthy absorption. Re-test after the next shutdown and compare corrected values.
Signature and date: tester |  |  |  |  | Reviewer
Method notes
1. Isolate and disconnect the winding or cable, and discharge it before and after the test. Keep leads clear of earth and of each other, and use the guard terminal where surface leakage may affect the reading.
2. Apply the test voltage continuously for 10 minutes and note the readings at the times shown. A hand-driven tester cannot hold voltage that long, so use a motor-driven or digital instrument for PI.
3. Record the winding temperature, not just the ambient temperature. Kt is an approximation and is most reliable when readings are compared at similar temperatures.
4. PI is not meaningful when the 1-minute reading is above about 5000 MΩ. Judge on the absolute reading and the trend instead.
5. Limits come from the Reference sheet (IEEE 43-2013 for rotating machines). Use the stricter of these and your plant or customer specification.

## Reference
REFERENCE: constants, limits and sources
Every number used by the Report sheet is listed here once. Blue cells can be edited if your standard or customer specification differs.
Enter data in the blue-on-yellow cells. Grey cells are calculated and locked (sheet protection has no password: Review > Unprotect Sheet).
A. Limits and constants used in the formulas
Item | Value | Unit | Basis
Pre-1970 windings, field windings and others: minimum IR = rated kV + this | 1 | MΩ per kV + 1 | IEEE 43-2013, minimum IR1min for windings not described below (kV + 1 MΩ)
Form-wound coils built after about 1970 (AC) and DC armatures: minimum IR | 100 | MΩ | IEEE 43-2013, minimum IR1min
Random-wound stator coils, and form-wound coils rated below 1 kV: minimum IR | 5 | MΩ | IEEE 43-2013, minimum IR1min
Minimum polarization index, thermal class A | 1.5 | - | IEEE 43-2013, minimum PI by thermal class
Minimum polarization index, thermal class B, F and H | 2 | - | IEEE 43-2013, minimum PI by thermal class
Reference temperature for correction | 40 | °C | IEEE 43-2013 refers readings to 40 °C
Temperature interval over which IR halves | 10 | °C | Usual field rule (Kt = 0.5^((40 - T)/10)). An approximation.
PI not meaningful when IR at 1 min exceeds | 5000 | MΩ | IEEE 43-2013 note on very high readings
DAR boundary: poor / questionable | 1 | - | Common guide band (CIE PI and DAR calculator), not a standard limit
DAR boundary: questionable / acceptable | 1.25 | - | Common guide band, not a standard limit
DAR boundary: acceptable / excellent | 1.6 | - | Common guide band, not a standard limit
PI boundary: dangerous / questionable | 1 | - | Common guide band (CIE PI and DAR calculator), not a standard limit
PI boundary: questionable / good | 2 | - | Common guide band, not a standard limit
PI boundary: good / excellent | 4 | - | Common guide band, not a standard limit
B. Recommended DC test voltage by winding rated voltage (IEEE 43-2013)
Rated line voltage up to (kV) | Test voltage from (V DC) | Test voltage to (V DC) | Band
1 | 500 | 500 | Below 1 kV (strictly less than)
2.5 | 500 | 1000 | 1 kV up to and including 2.5 kV
5 | 1000 | 2500 | Above 2.5 kV up to and including 5 kV
12 | 2500 | 5000 | Above 5 kV up to and including 12 kV
1000 | 5000 | 10000 | Above 12 kV
C. Sources, assumptions and limits of use
Sources: IEEE Std 43-2013, Recommended Practice for Testing Insulation Resistance of Electric Machinery (minimum IR, minimum PI, test voltages, temperature correction). The values above were entered from the standard as commonly quoted. Check them against the edition you work to before relying on a result.
These are recommended minimums for in-service rotating machines. They are not a guarantee of health, and a pass with a falling trend still deserves attention. Use the stricter of these limits and your plant or customer specification.
Temperature correction Kt = 0.5^((40 - T) / 10) is a field approximation. For best trending, test at a similar winding temperature each time and record the temperature.
The DAR and PI class names (Poor, Questionable, Good and so on) are common guide bands used by CIE tools, not limits from IEEE 43. Only the minimum PI in section A comes from the standard.
Leakage current at 1 minute is calculated as test voltage / IR (V divided by MΩ gives µA). It is an indication only, not a measurement of the instrument output current.
For cables, transformers and other equipment, use the limits in the relevant standard or manufacturer instruction and edit the blue cells above. The winding-class options on the Report sheet apply to rotating machines.