## Report
OVERCURRENT RELAY SECONDARY INJECTION TEST REPORT
Phase overcurrent (50/51): pickup, drop-off, inverse-time operating times and high-set element, with expected values calculated from the settings
Enter data in the blue-on-yellow cells. Grey cells are calculated and locked (sheet protection has no password: Review > Unprotect Sheet).
1. Job and equipment details
Customer / site |  |  |  | Feeder / panel ID
Relay make and model |  |  |  | Relay serial number
Test set model |  |  |  | Test set serial and calibration due
Test date |  |  |  | Auxiliary supply voltage
Tested by |  |  |  | Witnessed or reviewed by
2. Relay settings (from the setting sheet)
CT ratio: primary (A) |  |  |  | CT secondary (A)
Operating characteristic |  |  |  | Relay function tested
Pickup setting Is (A primary) |  |  |  | Time multiplier setting TMS
Definite-time delay (s), for the Definite time setting |  |  |  | High-set I>> (A primary)
High-set time delay (s)
Pickup Is on the secondary (A) |  |  |  | Curve constant k
High-set I>> on the secondary (A) |  |  |  | Curve constant alpha
3. Tolerances (from the relay datasheet or test specification)
Pickup tolerance (+/- %) |  |  |  | Timing tolerance (+/- % of expected)
Timing tolerance minimum (ms) |  |  |  | Reset (drop-off) ratio, minimum
High-set pickup tolerance (+/- %) |  |  |  | High-set time tolerance (+/- s)
Results show "Enter tolerance" until the matching tolerance is filled in. This template does not assume any tolerance. For timing, the allowed band is the larger of the percentage and the minimum in milliseconds.
4. Pickup and drop-off
Test | Expected (A sec) | Measured (A sec) | Error (%) or reset ratio | Result
Pickup (lowest current that starts the element)
Drop-off (current at which the element resets) | -
5. Operating time on the selected characteristic
Multiple of pickup (x Is) | Inject (A sec) | Expected time (s) | Measured time (s) | Error (%) | Allowed band (+/- s) | Result
2
3
5
10
20
Expected time = TMS x k / ((I / Is)^alpha - 1) for the inverse curves, or the definite-time delay. Inject the current shown, measure the operating time with the test set, and enter it. Keep multiples within the range the relay manufacturer states.
6. High-set element (I>>)
Test | Expected | Measured | Error | Result
High-set pickup (A sec)
High-set operating time (s), injected above I>>
7. Checks
Check | Status | Remarks
CT ratio and polarity verified against nameplate and drawings
Relay settings read back and match the approved setting sheet
Wiring and terminations checked against the schematic
Trip circuit continuity and trip coil supervision checked
Output contacts operate the circuit breaker (trip test)
Flags, LEDs and event records operate correctly
Insulation resistance of relay circuits measured per instructions
Test connections removed, relay returned to service state
8. Result
Tests passed | 0
Tests failed or checks marked Not OK | 0
Tests waiting for a tolerance | 0
Overall result
Remarks and recommended action
Signature and date: tester |  |  |  | Reviewer

## Example
OVERCURRENT RELAY SECONDARY INJECTION TEST REPORT
Phase overcurrent (50/51): pickup, drop-off, inverse-time operating times and high-set element, with expected values calculated from the settings
EXAMPLE with made-up data, to show the expected format. Use the blank sheet for your own report.
1. Job and equipment details
Customer / site | Demo Plant, Howrah |  |  | Feeder / panel ID |  | 11 kV feeder F-4 incomer
Relay make and model | Sample numerical overcurrent relay |  |  | Relay serial number |  | Sample serial
Test set model | Sample relay test set |  |  | Test set serial and calibration due |  | Sample serial, cal due Mar 2027
Test date | 2026-10-18 |  |  | Auxiliary supply voltage |  | 110 V DC
Tested by | A. Sample |  |  | Witnessed or reviewed by |  | B. Sample
2. Relay settings (from the setting sheet)
CT ratio: primary (A) | 200 |  |  | CT secondary (A) |  | 1
Operating characteristic | Standard inverse |  |  | Relay function tested |  | 50/51 phase overcurrent
Pickup setting Is (A primary) | 200 |  |  | Time multiplier setting TMS |  | 0.2
Definite-time delay (s), for the Definite time setting |  |  |  | High-set I>> (A primary) |  | 1200
High-set time delay (s) | 0.05
Pickup Is on the secondary (A) | 1 |  |  | Curve constant k |  | 0.14
High-set I>> on the secondary (A) | 6 |  |  | Curve constant alpha |  | 0.02
3. Tolerances (from the relay datasheet or test specification)
Pickup tolerance (+/- %) | 5 |  |  | Timing tolerance (+/- % of expected) |  | 5
Timing tolerance minimum (ms) | 30 |  |  | Reset (drop-off) ratio, minimum |  | 0.95
High-set pickup tolerance (+/- %) | 5 |  |  | High-set time tolerance (+/- s) |  | 0.03
Results show "Enter tolerance" until the matching tolerance is filled in. This template does not assume any tolerance. For timing, the allowed band is the larger of the percentage and the minimum in milliseconds.
4. Pickup and drop-off
Test | Expected (A sec) | Measured (A sec) | Error (%) or reset ratio | Result
Pickup (lowest current that starts the element) | 1 | 1.02 | 2% | PASS
Drop-off (current at which the element resets) | - | 0.97 | 0.95098 | PASS
5. Operating time on the selected characteristic
Multiple of pickup (x Is) | Inject (A sec) | Expected time (s) | Measured time (s) | Error (%) | Allowed band (+/- s) | Result
2 | 2 | 2.0058 | 2.03 | 1.206% | 0.10029 | PASS
3 | 3 | 1.2604 | 1.27 | 0.7628% | 0.063019 | PASS
5 | 5 | 0.85594 | 0.86 | 0.4739% | 0.042797 | PASS
10 | 10 | 0.59412 | 0.6 | 0.9897% | 0.03 | PASS
20 | 20 | 0.45347 | 0.46 | 1.44% | 0.03 | PASS
Expected time = TMS x k / ((I / Is)^alpha - 1) for the inverse curves, or the definite-time delay. Inject the current shown, measure the operating time with the test set, and enter it. Keep multiples within the range the relay manufacturer states.
6. High-set element (I>>)
Test | Expected | Measured | Error | Result
High-set pickup (A sec) | 6 | 6.1 | 1.667% | PASS
High-set operating time (s), injected above I>> | 0.05 | 0.055 | 0.005 | PASS
7. Checks
Check | Status | Remarks
CT ratio and polarity verified against nameplate and drawings | OK
Relay settings read back and match the approved setting sheet | OK
Wiring and terminations checked against the schematic | OK
Trip circuit continuity and trip coil supervision checked | OK
Output contacts operate the circuit breaker (trip test) | OK
Flags, LEDs and event records operate correctly | OK
Insulation resistance of relay circuits measured per instructions | N/A
Test connections removed, relay returned to service state | OK
8. Result
Tests passed | 9
Tests failed or checks marked Not OK | 0
Tests waiting for a tolerance | 0
Overall result | PASS - all 9 tests within tolerance
Remarks and recommended action | Example only. All points inside the entered tolerances. Tolerances here are sample values, take yours from the relay datasheet.
Signature and date: tester |  |  |  | Reviewer

## Reference
REFERENCE: operating characteristics, formulas and sources
Curve constants used by the Report sheet. Blue cells can be edited if your relay uses different constants.
Enter data in the blue-on-yellow cells. Grey cells are calculated and locked (sheet protection has no password: Review > Unprotect Sheet).
A. IEC inverse-time characteristics: t = TMS x k / ((I / Is)^alpha - 1)
Curve | k | alpha | Note
Standard inverse | 0.14 | 0.02 | IEC 60255-151 normal (standard) inverse
Very inverse | 13.5 | 1 | IEC 60255-151 very inverse
Extremely inverse | 80 | 2 | IEC 60255-151 extremely inverse
Long-time inverse | 120 | 1 | IEC 60255-151 long-time inverse
Definite time | 0 | 0 | Operating time is the definite-time delay you enter. k and alpha are not used.
B. Sources, assumptions and limits of use
Sources: IEC 60255-151, Measuring relays and protection equipment, Part 151: Functional requirements for over/under current protection (inverse-time characteristics and their constants). Check that your relay uses the same characteristic and edit the blue cells if the manufacturer defines it differently.
The formula applies for multiples of pickup above 1. Many relays limit the characteristic above a maximum multiple (often 20), so keep test points within the range the manufacturer states.
Tolerances (pickup, operating time, reset ratio, high-set) are entered on the Report sheet. This template does not assume them: take them from the relay datasheet or your test specification. Timing accuracy is often quoted as a percentage with a minimum value in milliseconds, so the sheet accepts both and uses the larger.
Secondary injection tests the relay and its settings. It does not prove CT ratio, polarity or wiring on its own, which is why those checks are on the checklist. Follow your site permit and safety procedure when testing.
The expected time for each test point is calculated from the settings, so the template is only as good as the settings you enter. Enter the pickup in primary amps and the CT ratio, and the sheet works out the secondary injection currents.